### Praesideo Basic Call Station LBB4430/00

### Architects’ and Engineers’ Specifications

The basic call station shall have a network interface for fiber optical hybrid cabling with dual network connections, capable of redundant loop operation. The fiber optic network interface of the call station shall support multi-channel digital audio and control signals.

The call station shall use a cardioid, supervised microphone on a gooseneck stem with good speech intelligibility. It shall have a limiter and a speech filter to improve speech intelligibility and prevent clipping of the audio signal. The call station shall contain a digital audio processor with a 3-band fully parametric equalizer and semi parametric shelving equalizers for bass and treble control, sensitivity control and a supervision pilot tone generator and detector to monitor the internal signal paths.

It shall have a monitoring loudspeaker with volume control and a 3.5 mm jack connection for a headset. Insertion of the headset connector shall automatically disconnect and replace the gooseneck microphone and internal loudspeaker. The chime and pre-recorded message parts of a call shall be audible via the loudspeaker or headset for monitoring by the operator.

It shall be possible to connect up to 16 call station keypads to the call station via a serial communication link. The call station shall provide the power supply for the keypads. The connected keypads shall provide various selection options for the call station.

The call station shall be remotely configurable via the network interface and it shall be powered from the network for easy installation.

The call station shall have a supervision system to monitor its functions and operation in compliancy to IEC 60849. Network connectivity status, operation status and fault conditions shall be displayed via LEDs on the unit. Fault conditions shall also be reported by the unit to a network connected system controller for logging purposes.

The call station shall support fail-safe operation, i.e. even if the controller of the audio system fails, the call station is still able to put through emergency calls to all audio outputs on the network.

The unit shall be able to operate at a maximum operating temperature of 45°C.

The call station shall be certified by an independent test agency, such as the German TÜV, for compliancy to the standards EN 60849 and EN 54-16 for emergency sound systems.

The basic call station shall be a Praesideo LBB4430/00, manufactured by Bosch Security Systems.