ISC-PPR1-W16

Professional Series PIR Detector
ARCHITECTURAL AND ENGINEERING SPECIFICATION

Section 281600 – Intrusion Detection

PART 2 – PRODUCTS

2.01	MANUFACTURER

A. Bosch Security Systems

130 Perinton Parkway

Fairport, New York 14450

Phone: +1(585) 223 4060

Fax: +1 (585) 223 9180

www.boschsecurity.com

B.	The specified product shall be manufactured by a firm whose quality system is in compliance with the I.S. /ISO 9001/EN 29001, QUALITY SYSTEM.

2.02	PIR Detector Requirements

A. The product specified shall be a PIR detector designed for commercial indoor applications. The unit shall consist of a self-locking two-piece enclosure with a built in two-way bubble level to help simplify the installation. The detector shall incorporate 1) sensor data fusion technology to ensure that the detector sends alarm conditions based only on precise information and 2) tri-focus optics technology to eliminate coverage gaps.

B.	The detector specified shall provide active white light suppression capable		of measuring the light intensity directed at the face of the unit and use 			the data gathered by the sensors to eliminate false alarms caused by the 			bright light source. False alarms shall not be caused from bright light 			sources up to 10,000 lux.

C.	The detector shall provide the following DIP switch selectable fields of			coverage:

1)	16 m x 21 m (50 ft x 70 ft)

2)	8 m x 10 m (26 ft x 33 ft)

D.	The detector shall be designed to be mounted at a height between 2.1 m to

3m (7 ft to 10 ft) and require no adjustments.

E.	The detector shall provide dynamic temperature compensation that adjusts 			the PIR sensitivity to identify human body heat accurately at critical 				temperatures to avoid false alarms and deliver consistent catch 							performance at all operating temperatures.

F.	The detector shall provide a cover and wall tamper switch with a normally-			closed contact that opens to notify the control panel in the event the 				cover is removed or the detector is	separated from the wall. The contacts 			shall be rated at 25 VDC, 125 mA maximum.

G. The detector shall contain a blue light emitting diode (LED) that adjusts 			automatically to the surrounding light level. The LED indicates alarms, and 		will activate during a walk test.

H.	The walk test LED may be enabled or disabled via a command from the control 		panel, or, it may be enabled or disabled using the local DIP switch of the 		detector.

I. The detector shall provide a solid state relay that is power supervised and 		uses less current and provides longer standby capacity than a mechanical 			relay. The solid state relay shall be used to send a silent alarm output 			signal. Rating of the relay shall be 3W, 125 mA, 25 VDC, with resistance 			less than 10 ohms.

J.	The detector shall reduce false alarms by having a sealed optic chamber 			that provides immunity to drafts and insects.

2.03	Sensor Technology Requirements

A.	The detector shall incorporate sensor data fusion technology that uses an 			internal 	microprocessor to gather, analyze, and compare the sensor data to 		make the most intelligent alarm decisions. The data processed from the 				microcontroller shall be from two pyroelectric sensors, a room temperature 		sensor, and a light level sensor.

B.	The detector shall also incorporate tri-focus technology that uses optics 			with three specific focal lengths: long-range coverage, middle-range 					coverage, and short-range coverage. The detector shall apply the three 				focal lengths to 86 detection zones which combine to produce 11 solid 				curtains of detection. The tri-focal optics technology shall include two 			pyroelectric sensors which deliver twice the standard optical gain.

2.04	Mounting Brackets

A.	The manufacturer shall offer the following three optional mounting brackets

1)	A Gimbal-mount bracket [Bosch B328] that mounts on a single-gang box and 		allows rotation of the detector.

2)	A Low profile plastic wall swivel mount bracket [Bosch B335-3]. The mount 		allows a vertical pivot range of +10º to -20º and a horizontal pivot 				range of ±25º.

3)	A plastic universal swivel bracket for ceiling mounting [Bosch B338]. The 		mount allows a vertical pivot range of +7º to -16º and a horizontal pivot 		of ±45º.

2.05	CERTIFICATIONS and APPROVALS

A. The specified detector is designed to comply with the following standards and approvals:

1)	UL639 and cULus

2) CE

3)	C-Tickº

4)	EN50131-1 Grade 2

2.06	MECHANICAL SPECIFICATIONS

A.	Dimensions: 127 mm x 69 mm x 58mm (5 in. x 2.75 in. x 2.25 in.)

B.	Material:	High impact ABS plastic.

C.	Color: white

2.07	ELECTRICAL SPECIFICATIONS

A.	Operating Voltage:	9 VDC to 15 VDC

B. 	Current (maximum): less than 15 mA

C.	Current (Standby):	less than 10 mA at 12 VDC

2.08	ENVIRONMENTAL SPECIFICATIONS

A.	Temperature, Operating and Storage: -30ºC to +55ºC (-20ºF to +130º F)

1) For UL Certified Installations:	 0ºC to +49ºC (+32ºF TO +120ºF).

B.	IP Rating:	IP 41, IK02 (EN60529, EN50102, EN50130-5 Class II)

C.	Relative humidity: 0 to 95%, non-condensing

The product specified shall be the Bosch Professional Series PIR Detector Model ISC-PPR1-W16

8/1/06		Specifications Subject to Change without Notice