April 2012

| Americas Bosch Security Systems, Inc. 130 Perinton Parkway Fairport, New York, 14450, USA Phone: + 1 800 289 0096 Fax: +1 585 223 9180 security.sales@us.bosch.com www.boschsecurity.us | Europe, Middle East, Africa Bosch Security Systems B.V. P.O. Box 80002 5600 JB Eindhoven, The Netherlands Phone: + 31 40 2577 284 Fax: +31 40 2577 330 emea.securitysystems@bosch.com www.boschsecurity.com | Asia-Pacific Robert Bosch (SEA) Pte Ltd, Security Systems 11 Bishan Street 21 Singapore 573943 Phone: +65 6571 2600 Fax: +65 6571 2698 apr.securitysystems@bosch.com www.boschsecurity.com |
| --- | --- | --- |

Product Guide Specification

SECTION 28 23 29

VIDEO SURVEILLANCE REMOTE DEVICES AND SENSORS

BOSCH VG5 AUTODOME 600 SERIES ANALOG CAMERAS

- – GENERAL

  - SUMMARY

    - Section Includes

      - Video Surveillance Remote Devices

    - Related Sections

      - Section [28 23 13 – Video Surveillance Control and Management Systems].

      - Section [28 23 16 – Video Surveillance Monitoring and Supervisory Interfaces].

      - Section [28 23 19 – Digital Video Recorders and Analog Recording Devices].

      - Section [28 23 23 – Video Surveillance Systems Infrastructure].

**********Specifier’s note: Include those standards referenced elsewhere in this SECTION.

  - REFERENCES

    - American National Standards Institute (ANSI) (www.ansi.org).

      - ANSI C63.4 Methods of Measurement of Radio-Noise Emissions from Low-Voltage Electrical and Electronic Equipment in the Range of 9 kHz to 40 GHz.

    - Australia and New Zealand Standards

      - AS/NZS 3548 Limits and methods of measurement of radio disturbance characteristics of information technology equipment.

    - Canadian Standards Association (CSA)

      - CAN/CSA E60950-1 Information Technology Equipment Safety.

    - European Norm

      - EN 50121-4 Railway Applications - Electromagnetic Compatibility - Part 4: Emission and Immunity of the Signaling and Telecommunications Apparatus.

      - EN 50130-4 Alarm Systems - Electromagnetic Compatibility - Product Family Standard: Immunity Requirements For Components Of Fire, Intruder And Social Alarm Systems.

      - EN 55022 class A (CE) – Information Technology Equipment – Radio Disturbance Characteristics – Limits and Methods of Measurement for Emission.

      - EN 55024 Information Technology Equipment (CE) – Immunity Characteristics – Limits and Methods of Measurement.

      - EN 60950 (CE) – Information Technology Equipment - Safety.

      - EN 61000-3-2 (CE) Electromagnetic Compatibility – Limits for Harmonic Current Emissions.

      - EN 61000-3-3 (CE) Electromagnetic Compatibility – Limits – Limitation of Voltage Changes, Voltage Fluctuations and Limitation of Voltage.

    - Federal Communications Commission (FCC) (www.fcc.gov)

      - FCC CFR 47 part 15 class A – Telecommunications – Radio Frequency Devices – Digital Device Emission.

    - International Electrotechnical Commission (IEC)

      - IEC 60529 Degrees of protection provided by enclosures (IP Code).

      - IEC 60950 Information Technology Equipment – Safety.

    - Institute of Electrical and Electronics Engineers, Inc. (IEEE) (www.ieee.org)

      - IEEE 802.3af Power Over Ethernet.

    - International Organization for Standardization (ISO)

      - 9001 – Quality System.

    - Underwriters Laboratories, Inc. (UL) (www.ul.com)

      - UL 50 Enclosures for Electrical Equipment.

      - UL 2043 Fire Test for Heat and Visible Smoke Release for Discrete Products and their Accessories Installed in Air-Handling Spaces.

      - UL 60950-1 Information Technology Equipment - Safety.

  - SYSTEM DESCRIPTION

    - Video Surveillance Remote Devices

      - Dome Day/Night PTZ CCD Analog camera

    - Performance Requirements

      - A day/night high-resolution CCD dome PTZ camera that offers 550 TVL and 12x digital zoom.

      - Progressive scan technology.

      - Sodium Vapor White Balance mode.

      - Provide 24 hour security with detail images – day or night.

      - Possesses advanced intelligence features.

      - Have different mounting versions.

  - SUBMITTALS

    - Submit under provisions of Section [01 33 00.]

    - Product Data:

      - Manufacturer’s data, user and installation manuals for all equipment and software programs including computer equipment and other equipment required for complete video management system.

    - Shop Drawings; include

      - System device locations on architectural floor plans.

      - Full Schematic of system, including wiring information for all devices.

    - Closeout Submittals

      - User manual.

      - Parts list.

      - System device locations on architectural floor plans.

      - Wiring and connection diagram.

      - Maintenance requirements.

  - QUALITY ASSURANCE

    - Manufacturer:

      - Minimum of [10] years experience in manufacture and design Video Surveillance Devices.

      - Manufacturer’s quality system: Registered to ISO 9001 Quality Standard.

    - Video Surveillance System

      - Listed by [UL] [EN] [FCC] specifically for the required loads.  Provide evidence of compliance upon request.

    - Installer:

      - Minimum of [5] years experience installing Video Surveillance System.

  - DELIVERY, STORAGE AND HANDLING

    - Comply with requirements of Section [01 60 00].

    - Deliver materials in manufacture’s original, unopened, undamaged containers; and unharmed original identification labels.

    - Protect store materials from environmental and temperature conditions following manufacturer’s instructions.

    - Handle and operate products and systems according to manufacturer’s instructions.

    - Bosch provides off-the-shelf availability for our top selling products and same-day or 24-hour shipping.

  - WARRANTY

    - Provide manufacturer’s warranty covering [3] years for replacement and repair of defective equipment.

  - MAINTENANCE

    - Make ordering of new equipment for expansions, replacements, and spare parts available to dealers and end users.

    - Provide factory direct technical support from 8:00 a.m. to 8:00 p.m. via phone and e-mail.

- – PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:

[Bosch Security Systems, Inc.

130 Perinton Parkway

Fairport, New York, 1450, USA

Phone: + 1 800 289 0096

Fax: + 1 585 223 9180

security.sales@us.bosch.com

www.boschsecurity.us]

[Bosch Security Systems B.V.

P.O. Box 80002

5600 JB Eindhoven, The Netherlands

Phone: + 31 40 2577 284

Fax: +31 40 2577 330

emea.securitysystems@bosch.com

www.boschsecurity.com]

[Asia-Pacific

Robert Bosch (SEA) Pte Ltd, Security Systems

11 Bishan Street 21

Singapore 573943

Phone: +65 6258 5511

Fax: +65 6571 2698

apr.securitysystems@bosch.com

www.boschsecurity.com]

    - Substitutions: [Not permitted.] [Under provisions of Division 1.]

      - [All proposed substitutions must be approved by the Architect or Engineer professional.]

      - [Proposed substitutions must provide a line-by-line compliance documentation.]

**********Specifier’s note: Select Camera System Series based on project requirement.

  - BOSCH VG5 AUTODOME 600 SERIES ANALOG CAMERA [VG5-613-CCS] 
[VG5-623-CTS] [VG5-613-ECS] [VG5-613-PCS] [VG5-614-ECS] [VG5-614-PCS]
[VG5-623-ECS] [VG5-623-PCS] [VG5-624-ECS] [VG5-624-PCS]

    - General Characteristics:

      - The day/night PTZ camera shall offer a 28x or 36x 1/4-in. Exview HAD CCD camera with 12x digital zoom.

      - The day/night PTZ camera shall offer wide dynamic range technology that allows for the capture of clear from both light and dark areas in the same scene.

      - The day/night PTZ camera shall offer progressive scan technology that allows for the capture of clear images from a moving camera.

      - The day/night PTZ camera shall offer a Wide Dynamic Range of 92 dB for clear images in extreme high-contrast environments.

      - The day/night PTZ camera shall feature a Sodium Vapor White Balance mode for taking images under a street lamp or tunnel lamp.

      - The day/night PTZ camera shall offer automated motion tracking system that uses an advanced DSP that provides real-time video processing for object tracking.

      - The day/night PTZ camera shall be able to create a “region of interest” within a preset position where motion is to be detected.

      - The day/night PTZ camera shall allow virtual masks to ignore areas of unwanted motion.

      - The day/night PTZ camera shall support the following tour modes:

        - 99 user-defined pre-positions with 20-character titles.

        - One (1) preset tour capable of 99 pre-positions and a configurable dwell time between positions.

        - One (1) AutoPan mode.

        - Two (2) recorded tours, which have a combined duration of 15 minutes of movements. These are recorded macros of an operator’s movements, including pan, tilt, and zoom activities, and can be played back in a continuous manner.

      - The day/night PTZ camera shall provide pan and tilt preset repeatability accurate to within ±0.1 degrees.

      - The day/night PTZ camera shall provide the following variable pan/tilt speeds

        - A range of 0.1 degrees per second to 120 degrees per second.

        - A pan speed of 360 degrees per second between prepositions

        - A tilt speed of 100 degrees per second between prepositions.

      - The day/night PTZ camera shall provide a pan range of 360 degrees of continuous rotation.

      - The day/night PTZ camera shall provide the patented Bosch AutoScaling (proportional zoom) and AutoPivot features.

      - The day/night PTZ camera shall provide 16 independent sectors with 20-character titles/sector.

      - The day/night PTZ camera shall provide 24 individual privacy masks with the following features:

        - Shapes shall be defined with five corners.

        - The mask shall be black, white, or blurred.

      - The day/night PTZ camera shall offer an optional fiber optic kit.

      - The day/night PTZ camera shall be able to be mounted to a wall, mounted to a surface, mounted to a pipe, or recessed into an indoor ceiling.

      - The day/night PTZ camera shall offer IP66 environmental protection for pendant models and IP54 protection for in-ceiling models.

      - The day/night PTZ camera dome bubble shall:

        - Meet flame, crush, and impact resistant requirements able to exceed UL 746C standard for polymeric material enclosures.

        - [Be a high-resolution bubble made of acrylic]

        - [Be an impact-resistant bubble made of 2.6 mm thick polycarbonate able to withstand a 100 foot-pound impact or the equivalent of a 10 lb sledgehammer dropped from a height of 10 feet.]

        - Offer a clear or tinted version.

    - Basic Features:

      - The day/night PTZ camera shall provide a fast address method to allow the camera address number used for control to be remotely programmed from the system keyboard.

      - The day/night PTZ camera shall ensure that any advanced commands required to program the dome are accessed via three levels of password protection ranging from low to high.

      - The day/night PTZ camera shall provide a feature that automatically rotates, or pivots, the camera to simplify tracking of a person walking directly under the camera.

      - The day/night PTZ camera shall provide advanced troubleshooting and diagnostics via diagnostic LEDs and on-screen diagnostic displays.

      - The day/night PTZ camera shall possess on-screen display menus that support English, Czech, Dutch, French, German, Italian, Polish, Portuguese, Russian, and Spanish.

      - The day/night PTZ camera shall allow an optional integral fiber optic transceiver module, capable of transmitting and receiving video and Biphase signals up to 2.5 miles (4 km). The fiber optic module is compatible with 50/125 mm, 62.5/125 mm, low-loss multimode glass fiber, rated for minimum system bandwidth of 20 MHz (video 850 nm/data 1300 nm).

      - The day/night PTZ camera shall be compatible with Bosch Allegiant series switcher/controller, Bosch Video Recorders, and Divar digital video recorders.

    - Advanced Features

      - The day/night PTZ camera shall provide fast 360º per second camera pan and 100º per second tilt speeds.

      - The day/night PTZ camera shall divide the cameras 360º rotation into 16 independent sectors with 20-character titles per sector. Any or all of the 16 sectors can be blanked from the operator's view.

      - The day/night PTZ camera shall offer the ability to define 24 masks with up to 8 masks per scene that prohibit areas of the field of view from being seen even if the camera is panned, tilted, or zoomed.

      - The masks shall be shaped using three (3), four (4) or five (5) anchor points to form different shapes to best fit the area to be masked. Mask selections shall be black, white or blurred.

      - The day/night PTZ camera shall have a preset tour function.

      - The day/night PTZ camera shall store up to 99 preset scenes with each preset programmable for 20 character titles.

      - The day/night PTZ camera shall offer one (1) preset tour to display consecutively the preset scenes for a programmed dwell time. Any or all of the presets can be included or excluded from the tour.

      - The day/night PTZ camera shall allow the recording of two (2) separate tours of an operator's keyboard movements consisting of tilt and zoom activities, for a total combined duration time of 15 minutes. The recorded tours can be continuously played back.

      - The day/night PTZ camera shall execute one of the following programmable options when an operator stops manual control of the camera, and a programmed period of time is allowed to expire: return to a stored preset number, return to the automated tour previously executed, and do nothing.

    - Alarm Handling

      - The day/night PTZ camera shall provide advanced alarm handling to manage up to seven (7) alarm inputs and four (4) alarm outputs by means of a programmable "Rules" engine.

      - The day/night PTZ camera shall allow any or all of the input contacts to be programmed upon activation to automatically move the camera to any preposition location, close an output relay for a programmed period of time, transmit an alarm signal (via Bilinx) and display an alarm indication on the on-screen display of the monitor.

    - Motion Detection and Tracking

      - The day/night PTZ camera shall provide enhanced automatic motion tracking using a dedicated digital signal processor (DSP) for smooth object tracking.

      - The day/night PTZ camera shall have the ability to follow an object continually when passing behind a privacy mask.

      - The day/night PTZ camera shall use Virtual Masking technology to ignore areas of extraneous background motion.

      - The day/night PTZ camera shall provide video motion detection (VMD) that can be configured to create a region of interest within multiple preset positions where motion is to be detected.

      - The day/night PTZ camera shall support a total of 10 individual regions of interest (one per preset position).

    - Image Processing

      - The day/night PTZ camera shall provide image stabilization using a dedicated digital signal processor (DSP) to minimize camera shake on both the horizontal and vertical axes while maintaining a clear image as the zoom range increases. The image stabilization algorithms do not reduce camera sensitivity.

      - The day/night PTZ camera shall provide an AutoPivot feature to automatically rotate and flip the camera as it tilts through the vertical position to maintain the correct orientation of the image.

      - The day/night PTZ camera shall provide an AutoScaling feature that reduces the pan/tilt speed as the camera zooms in on an object, so that the relative speed on the screen remains constant.

    - Camera Options

      - Bosch VG5-6x3 Series

        - The 28x day/night camera shall consist of an integrated high resolution Exview HAD CCD camera using a 1/4-inch imager.

        - The 28x day/night camera shall offer the following effective picture elements:

          - PAL: Approx. 440,000; 752(H) x 582(V)

          - NTSC: Approx. 380,000; 768 (H) x 494 (V)

        - The 28x day/night camera shall offer a 28x (3.5 – 98.0 mm, F1.35 to F3.7) auto-iris, auto-focus optical zoom lens. It will have a variable high speed, 360º pan/tilt drive with a top speed of 120( per second.

        - The 28x day/night camera shall be designed to perform over a wide range of environmental and lighting conditions with a horizontal resolution of 550 TVL (NTSC/PAL).

        - The day/night PTZ camera shall offer a Wide Dynamic Range of 92 dB for clear images in extreme high-contrast environments.

        - The 28x day/night camera shall offer sensitivity down to 0.02 lux in day mode, and 0.0026 lux in night mode.

        - The 28x day/night camera shall switch automatically from daylight color operation to a higher sensitivity nighttime monochrome mode when light levels fall below an adjustable threshold level. Day/night operation may also be manually switched on or off from the system switcher/controller keyboard.

        - The 28x day/night camera shall possess a full 12x digital zoom that is functional once the maximum 28x optical zoom limit has been reached. The 12x digital zoom lens is on/off selectable from the system controller keyboard.

        - The 28x day/night camera shall have a Freeze Frame feature that holds a preposition shot while moving to another preposition.

        - The 28x day/night camera shall offer color correction for images lit with a sodium vapor lamp.

        - The 28x day/night camera shall conform to the following specifications:

          - Horizontal Resolution: 550 TVL (NTSC/PAL)

          - Sensitivity:

            - Day Mode (30 IRE):  F1.6, 1/60 (1/50) shutter, max AGC

SensUp Off: 0.33 lux

SensUp On (NTSC: 1/4s, 15x; PAL 1/3s, 16.7x): 0.02 lux

            - Day Mode (50 IRE):  F1.6, 1/60 (1/50) shutter, max AGC

SensUp Off: 0.66 lux

SensUp On (NTSC: 1/4s, 15x; PAL 1/3s, 16.7x): 0.04 lux

            - Night Mode (30 IRE):  F1.6, 1/60 (1/50) shutter, max AGC

SensUp Off: 0.066 lux

SensUp On (NTSC: 1/4s, 15x; PAL 1/3s, 16.7x): 0.0026 lux

            - Night Mode (50 IRE):  F1.6, 1/60 (1/50) shutter, max AGC

SensUp Off: 0.166 lux

SensUp On (NTSC: 1/4s, 15x; PAL 1/3s, 16.7x): 0.0082 lux

          - Electronic Shutter Speed (AES): 1 to 1/10,000 sec.

          - Wide Dynamic Range: 92 dB

          - Lens: 3.5 mm to 98.0 mm, (F1.35 to F3.7)

          - Optical Zoom: 26x

          - Digital Zoom: 12x

          - Video Output: 1.0Vp-p, 75 ohms

          - Synchronization: Line-lock (-120( to 120( vertical phase adjust) or internal crystal.

          - Signal to Noise Ratio: Greater than 50 dB

          - White Balance: 2,000 K to 10,000 K

      - Bosch VG5-6x4 Series

        - The 36x day/night camera shall consist of an integrated high resolution Exview HAD CCD camera using a 1/4-inch imager.

        - The 36x day/night camera shall offer the following effective picture elements:

          - PAL: Approx. 440,000; 752(H) x 582(V)

          - NTSC: Approx. 380,000; 768 (H) x 494 (V)

        - The 36x day/night camera shall offer a 36x (3.4 – 122.4 mm, F1.6 to F4.5) auto-iris, auto-focus optical zoom lens with manual override. It will have a variable high speed, 360º pan/tilt drive with a top speed of 120º per second.

        - The 36x day/night camera shall be designed to perform over a wide range of environmental and lighting conditions with a horizontal resolution of 550 TVL (NTSC/PAL) typical.

        - The day/night PTZ camera shall offer a Wide Dynamic Range of 92 dB for clear images in extreme high-contrast environments.

        - The 36x day/night camera shall offer sensitivity down to 0.04 lux in day mode, and 0.0052 lux in night mode.

        - The 36x day/night camera shall switch automatically from daylight color operation to a higher sensitivity nighttime monochrome mode when light levels fall below an adjustable threshold level. Day/night operation may also be manually switched on or off from the system switcher/controller keyboard.

        - The 36x day/night camera shall possess a full 12x digital zoom that is functional once the maximum 36x optical zoom limit has been reached. The 12x digital zoom lens is on/off selectable from the system controller keyboard.

        - The 36x day/night camera shall have a Freeze Frame feature that holds a preposition shot while moving to another preposition.

        - The 36x day/night camera shall offer color correction for images lit with a sodium vapor lamp.

        - The 36x day/night camera shall conform to the following specifications:

          - Horizontal Resolution: 550 TVL (NTSC/PAL)

          - Sensitivity:

            - Day Mode (30 IRE):  F1.6, 1/60 (1/50) shutter, max AGC

SensUp Off: 0.66 lux

SensUp On (NTSC: 1/4s, 15x; PAL 1/3s, 16.7x): 0.04 lux

            - Day Mode (50 IRE):  F1.6, 1/60 (1/50) shutter, max AGC

SensUp Off: 1.4 lux

SensUp On (NTSC: 1/4s, 15x; PAL 1/3s, 16.7x): 0.1 lux

            - Night Mode (30 IRE):  F1.6, 1/60 (1/50) shutter, max AGC

SensUp Off: 0.104 lux

SensUp On (NTSC: 1/4s, 15x; PAL 1/3s, 16.7x): 0.0052 lux

            - Night Mode (50 IRE):  F1.6, 1/60 (1/50) shutter, max AGC

SensUp Off: 0.209 lux

SensUp On (NTSC: 1/4s, 15x; PAL 1/3s, 16.7x): 0.103 lux

          - Electronic Shutter Speed (AES): 1 to 1/10,000 sec.

          - Wide Dynamic Range: 92 dB

          - Lens: 3.4 mm to 122.4 mm (F1.6 to F4.5)

          - Optical Zoom: 36x

          - Digital Zoom: 12x

          - Video Output: 1.0 Vp-p, 75 ohms.

          - Synchronization: Line-lock (-120( to 120( vertical phase adjust) or internal crystal

          - Signal to Noise Ratio: Greater than 50 dB

          - White Balance: 2,000 K to 10,000 K

    - Camera Communications

      - Standard Communications

        - The day/night PTZ camera shall support a variety of data transmission methods, including Bilinx (over coax and UTP) and fiber.

        - The day/night PTZ camera shall allow remote control, configuration, and firmware updates over the cables.

        - The day/night PTZ camera shall possess a cable compensation feature that provides extended coaxial and UTP distance runs while preventing the image quality degradation caused by signal losses form long cable lengths.

        - The day/night PTZ camera shall natively support the following protocols:

          - Pelco “P”

          - Pelco “D”

      - [Bosch Alternative protocol communications module VG4-MTRN-C

        - The day/night PTZ camera shall supports these protocols:

          - American Dynamics Manchester

          - American Dynamics Sensormatic RS-422]

      - [Bosch Fiber Optic transceiver kit

        - The day/night PTZ camera shall offer an optional analog, multimode fiber optic conversion kit.

        - The integral fiber optic transceiver module shall transmit and receive video and Biphase signals up to 2.5 miles (4 km).

        - The integral fiber optic transceiver module shall be compatible with 50/125 µm, 62.5/125 µm, low loss multimode glass fiber, rated for minimum system bandwidth of 20 MHz (video 850 nm/data 1300 nm).]

    - Housing Options

      - The day/night PTZ camera shall be offered in Outdoor Pendant, Indoor Pendant, and In-Ceiling housings.

      - The day/night PTZ camera housings shall come standard with recessed setscrews and a recessed bubble latch for increased tamper resistance.

      - The day/night PTZ camera shall provide built-in surge protection for power, data, and video and alarm inputs.

      - [The Outdoor pendant housing shall:

        - Use a hinge, in-place of a tether, to make installation easier and safer.

        - Come with an attached sunshield.

        - Allow camera to view 18º above the horizon.

        - Conform to IP66 and NEMA 4X standards for a rugged and weather-resistant package.

        - Be made of cast aluminum for corrosion resistance, and supplied with a built-in heater/blower to provide an operating temperature range down to 
-40º C to 50º C (-40º F to 122º F).

        - [Be capable of extending the temperature range to –60°C to 50°C 
(–76°F to 122°F) with the optional VG4-SHTR-XT kit.]

        - Use a low-impact, high-resolution acrylic bubble.]

      - [The Indoor pendant housing shall:

        - Use a hinge, in-place of a tether, to make installation easier and safer.

        - Allow camera to view 18º above the horizon.

        - Conform to IP66 and NEMA 4X standards for a rugged and weather-resistant package.

        - Be made of cast aluminum for corrosion resistance.

        - Use a low-impact, high-resolution acrylic bubble.]

      - [The In-ceiling housing shall:

        - Allow camera to view 1º above the horizon.

        - Be Plenum rated and Conform to IP54 standards with the optional VGA-IP54K-IC installation kit.

        - Be made of cast aluminum for corrosion resistance.

        - Use a high-impact impact-resistant polycarbonate rugged bubble.

        - The rugged bubble shall be capable of withstanding impacts equivalent to a 4.5 kg (10 lb) eight dropped from a height of 3 m (10 ft).]

    - Electrical:

      - Camera input voltage/power requirements: 21 – 30 VAC, 50/60 Hz

      - Heater input voltage/power requirements: 21 – 30 VAC, 50/60 Hz

      - Power Draw (Typical):

        - [Indoor: 15 W / 27 VA]

        - [Outdoor: 51 W / 55 VA]

        - [Outdoor with XT kit: 67 W]

      - Surge Suppression (Protection)

        - Video: Peak current 10kA (Gas Tube Arrester), peak power 1000 W (10/1000(s)

        - Power Input (Dome): Peak current 7.3 A, peak power 600 W (10/1000(s)

        - Power Output (Arm Power Supply): Peak current 21.4 A, peak power 
1500 W (10/1000(s)

        - Alarm Inputs: Peak current 17 A, peak power 300 W (8/20(s)

        - Alarm Outputs: Peak current 2 A, peak power 300 W (8/20(s)

        - Relay Outputs: Peak current 7.3 A, peak power 600 W (10/1000(s)

    - Mechanical:

      - [In-Ceiling model

        - Weight: 2.66kg (5.86 lb)

        - Pan Range: 360( continuous

        - Tilt Angle: 1( above horizon

        - Power: 21 – 30 VAC, 50/60 VA

        - Variable Speed: 0.1(/s to 120(/s

        - Pre-position Speed: Pan: 360(/s Tilt: 100(/s

        - Preset Accuracy: +/-0.1(]

      - [Indoor Pendant model

        - Weight: 2.88 kg (6.3 lb).

        - Pan Range: 360( continuous.

        - Tilt Angle: 18( above horizon.

        - Power: 21 – 30 VAC, 50/60 Hz.

        - Variable Speed: 0.1(/s to 120(/s

        - Pre-position Speed: Pan: 360(/s Tilt: 100(/s

        - Preset Accuracy: +/-0.1(]

      - [Outdoor Pendant model

        - Weight: 3.32 kg (7.3 lb).

        - Pan Range: 360( continuous.

        - Tilt Angle: 18( above horizon.

        - Power: 21 – 30 VAC, 50/60 Hz.

        - Variable Speed: 0.1(/s to 120(/s

        - Pre-position Speed: Pan: 360(/s Tilt: 100(/s

        - Preset Accuracy: +/-0.1(]

    - Environmental:

      - Design Rating

        - [In-ceiling: Plenum, IP54 (with optional VGA-IP54K-IC)]

        - [Pendant, all models: IP66, NEMA 4X]

      - Operating Temperature:

        - [In-ceiling: –10°C to 40°C (14°F to 104°F)]

        - [Indoor Pendant: –40( to 50(C (–40( to 122(F)]

        - [Outdoor Pendant: –40( to 50(C (–40( to 122(F)]

        - [Outdoor Pendant with XT kit: –60°C to 50°C (–76°F to 122°F)]

      - Storage Temperature, all models: –40( to 60(C (–40( to 140(F)

      - Operating Humidity:

        - [In-ceiling: 0% to 90% relative, non-condensing]

        - [Indoor Pendant: 0% to 90% relative, non-condensing]

        - [Outdoor Pendant: 0% to 100% relative, non-condensing]

  - ACCESSORIES

    - Bubbles

      - In-ceiling

        - Bosch VGA-BUBBLE-CCLR Clear rugged polycarbonate

        - Bosch VGA-BUBBLE-CTIR Tinted rugged polycarbonate

      - Pendant

        - Bosch VGA-BUBBLE-PCLR Clear rugged polycarbonate

        - Bosch VGA-BUBBLE-PTIR Tinted rugged polycarbonate

        - Bosch VGA-BUBBLE-PCLA Clear high-resolution acrylic

        - Bosch VGA-BUBBLE-PTIA Tinted high-resolution acrylic

    - Mounts

      - Bosch VGA-ROOF-MOUNT Roof mount, white

      - Bosch VG4-A-9543 Pipe mount, white

      - Bosch VG4-A-PA0 Pendant arm mount 24 VAC, white

      - Bosch VG4-A-PA1 Pendant arm mount with 120 VAC transformer, white

      - Bosch VG4-A-PA2 Pendant arm mount with 230 VAC transformer, white

      - Bosch VGA-PEND-ARM Pendant arm without power supply box, white

      - Bosch VGA-PEND-WPLATE Pendant arm mounting plate for use with 
VGA-PEND-ARM, white

      - Bosch VG4-A-TSKIRT Trim skirt for AutoDome power supply box, white

      - Optional Mounting Accessories

        - For Roof Mounts

          - Bosch LTC 9230/01Flat Roof Adapter for Parapet Mount

        - For Arm Mounts

          - Bosch VG4-A-9542 Corner Mounting Plate

          - Bosch VG4-A-9541 Mast (Pole) Mounting Plate

    - In-ceiling Support Kits

      - Bosch VGA-IC-SP Bracket for suspended or drop ceilings

      - Bosch VGA-IP54K-IC Gasket kit for IP54 certification

    - Power Supplies

      - Bosch VG4-A-PSU0 Outdoor Power Supply Box, no transformer

      - Bosch VG4-A-PSU1 / VG4-A-PSU2 Outdoor Power Supply Box (120/230 VAC Transformer)

    - Bosch VGA-FIBER-AN Fiber Optic Kit

    - Bosch VG4-SHTR-XT Extended Heating Kit

- – EXECUTION

  - EXAMINATION

    - Examine areas to receive devices and notify adverse conditions affecting installation or subsequent operation.

    - Do not begin installation until unacceptable conditions are corrected.

  - PREPARATION

    - Protect devices from damage during construction.

  - INSTALLATION

    - Install devices in accordance with manufacturer’s instruction at locations indicated on the floor drawings plans.

    - Perform installation with qualified service personnel.

    - Install devices in accordance with the National Electrical Code or applicable local codes.

    - Ensure selected location is secure and offers protection from accidental damage.

    - Location must provide reasonable temperature and humidity conditions, free from sources of electrical and electromagnetic interference.

  - FIELD QUALITY CONTROL

    - Test snugness of mounting screws of all installed equipment.

    - Test proper operation of all video system devices.

    - Determine and report all problems to the manufacturer’s customer service department.

  - ADJUSTING

    - Make proper adjustment to video system devices for correct operation in accordance with manufacturer’s instructions.

    - Make any adjustment of camera settings to comply with specific customer’s need.

  - DEMOSTRATION

    - Demonstrate at final inspection that video management system and devices functions properly.

END OF SECTION

# Text boxes

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, based on MasterFormat 2004 and The Project Resource Manual—CSI Manual of Practice. The Manufacturer is responsible for technical accuracy.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Words and sentences within brackets [ ] are choices to include or exclude a particular item or statement.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.